## Slide 1: Dynamic Modelling First Principles Models Simple Systems I
Lectures on
CHEMICAL PROCESS CONTROL
Theory and Practice
Module 3.2.1

## Slide 2: Heated Surge Vessel
ASSUMPTIONS
Well mixed
No heat loss
Constant properties
Constant V and F0
Q given
F0, cA0, T0
F, cA, T
Q
PROBLEM
cA response to change in cA0
T response to change in T0
T response to change in Q
Material Balance
IC:
Energy Balance
IC:
First order ODE
Gain
Time constant
Time Constant
Time Constant
Gain
F0, cA0, T0
F, cA, T
Depend on operating conditions

## Slide 3: Heated Surge Vessel Dynamic Responses
1m3/min, 10 kmol/m3
20 oC
60 oC
10 m3
81.6 MJ/min
Cp = 2.55 kJ/kg K
ρ = 800 kg/m3

## Slide 4: Heated Surge Vessel Proportional Temperature Control
F0, cA0, T0
F, cA, T
TC
TSP
Using Deviation Variables
Regulator Step Response
Servo Step Response
Process Dynamic Model
Controller Equation

## Slide 5: Heated Surge Vessel Proportional Temperature Control: Dynamic Response
OBSERVATIONS
Smooth exponential response
Response speed increases with KC
Aggression in Q increases with KC
Steady state offset from TSP
Offset magnitude decreases with KC

## Slide 6: Exercise
F0
F
A P controller manipulates outflow F to hold tank level
  Obtain servo response (level setpoint step change)
  Obtain regulator response (F0 step change)

## Slide 7: Summary
Dynamics of very simple systems described by a first order ODE
First order ODE is parameterized by gain and time constant
  Gain and time constant change with operating conditions
    Usually decrease with throughput
  Response is usually described by a decaying exponential (e-at)
  First order ODE solved using integrating factor approach
Proportional control of a first order system
  Dynamics described by a first order ODE
  ODE parameters depend on operating conditions (K and τ) and controller gain (KC)
  Gives smooth dynamic response
  Results in offset from a constant setpoint
  Higher controller gain causes
    CV response time constant to decrease
    Lower offset from CV setpoint