## Slide 1: Advanced Controller Structures Cascade Control
Module 4.8.2
Lectures on
CHEMICAL PROCESS CONTROL
Theory and Practice

## Slide 2: Cascade Control
Master (primary) controller sets setpoint of a slave (secondary) controller. Slave output PV is strongly related to the master output PV
CSTR Temperature Control
LC
TT
TC
TC
TT
FC
TC
CC
Column Composition Control

## Slide 3: Why and Tuning
Pros
  Speeds up primary PV control
  Slave loop removes local disturbances
  Slave loop removes local non-linearities
Cons
  More instrumentation and loops to be tuned
Tuning
  Inside-out
  Tune innermost first (outer loops on manual)
  Then tune next outer loop (inner loops on auto)
  Inner loops may be P only (for higher controller gain than PI)
Slave loop dynamic speed >> Master loop dynamic speed

## Slide 4: Series Cascade
Gcs
Σ
ysSP
-1
Gpm
Σ
dm
ym
Gps
Σ
ys
ds
u
Gcm
-1
Σ
ymSP
Slave Loop
Master Loop

## Slide 5: Parallel Cascade
Gcs
Σ
ysSP
-1
Σ
Gcm
-1
ymSP
Slave Loop
Master Loop
Gpm
dm
Gps
Σ
ys
ds
u
Σ
ym

## Slide 6: Example
SERIES CASCADE CONTROLLER DESIGN
Slave controller is P only. Master controller is PI.
Slave and master controllers tuned for ξ = 0.5.
Master controller τI chosen to cancel dominant open loop pole.
Compare performance with a simple PI controller tuned for ξ = 0.5.
CLCE:
For ξ = 0.5 (ie φ = cos-1 ξ = 60°), s = -a + √3aj satisfies CLCE
Conjugate pair CLCE roots are
By conservation of roots, third root is
SLAVE CONTROLLER DESIGN

## Slide 7: Examplecontinued
MASTER CONTROLLER DESIGN
Use
Open loop roots:
CLCE: 125
Let s = -a + bj satisfy CLCE. From root locus, a < 0.2
Angle condition must be satisfied for s to lie on root locus
Put b=√3a (for ξ = 0.5) and solve for a iteratively to get
CLCE dominant root pair is
By magnitude condition
CASCADE CONTROLLER DESIGN
Slave Loop: Kc = 0.5 (P only) Kc = 0.1875 τI = 1 min
Master Loop: Kc = 0.6323 τI = 5 min Kc = 0.2815 τI = 5 min

## Slide 8: Examplecontinued
FEEDBACK CONTROLLER DESIGN
Use
Open loop roots:
CLCE: 125
Let s = -a + bj satisfy CLCE. From root locus, a < 0.2
Angle condition must be satisfied for s to lie on root locus
Put b=√3a (for ξ = 0.5) and solve for a iteratively to get
CLCE dominant root pair is
By magnitude condition

## Slide 9: Example: Dynamic Results

## Slide 10: Summary
Cascade control
  Used when controlling a secondary (fast) PV helps regulate a primary (slow) PV
  Set point of slave (fast) loop remotely set by master (slow) loop
  Inside-out tuning
Slave loop
  Removes local disturbances
  Removes local non-linearities
    Flow controller mitigates valve non-linear characteristic
  Somewhat speeds up the master loop response
Slave loop dynamic speed >> Master loop dynamic speed
Very commonly employed in process industry due to time scale separation