## Slide 1: Advanced Controller Structures Miscellaneous Structures Valve Positioning, Override, Split-Range, Selective
Module 4.8.3
Lectures on
CHEMICAL PROCESS CONTROL
Theory and Practice

## Slide 2: Valve Positioning or Optimizing Control
Keeps a valve nearly fully open (or closed) to optimize an economic objective function
  Requires clear process insight to develop the ‘optimizing’ control strategy
Common Examples
  Floating pressure control in a column
  Maximizing throughput in a cooling capacity limited reactor
  Minimizing RPM of a utility supply pump

## Slide 3: VPC Example 1
Column Condenser Valve Position Control
Used in difficult separations (tall towers) to reduce reboiler duty
Operate column at as low a pressure as possible
Separation is then easier
Reboiler duty would then be lower for same degree of separation
Since condenser sets column pressure, operate column such that condenser valve is nearly fully open

## Slide 4: VPC Example 1 continued
Column VPC
PC
VPC
80%
Ensures column operation at near open condenser valve
20% back-off given to ensure pressure control during surges
VPC can be a slow pure I controller

## Slide 5: VPC Example 2
Maximizing throughput in a cooling capacity limited exothermic CSTR
Cooling Water in
Fresh feed reactant
Cooling
Water out
TT
TT
TC
TC
FC
FC
VPC
80%
Ensures tight reactor temperature control
CSTR operates at near full cooling capacity
20% backoff for guaranteeing temperature control
VPC may be a slow I controller

## Slide 6: VPC Example 3
Minimizing High Wattage Variable Speed Pump Power
VPC
80%
FC
Fdemand
Unnecessary ΔP across valve if not near fully open. Implies pump RPM too high.
Adjust pump RPM such that valve is nearly fully open. Ensures near minimum power consumption
20% back-off to ensure ability to meet Fdemand surge

## Slide 7: Override Control
Two or more controllers compete for manipulating a control valve
The control configuration (or structure) in not fixed and changes depending on operating scenario
Structural changes become necessary to ensure proper process regulation
  Usually driven by safety concerns
    Eg cut down reboiler steam as column sump level goes too low
  Loss of control dof due to a unit maxing out
    Usually requires inventory (material balance) control system reconfiguration
Reset windup protection necessary when competing controllers are PI

## Slide 8: Overrides Example 1
Distillation Column Steam Valve Manipulation
FC
LS
TC
ΔPC
OLC
20%
LC
50%
Normally, steam valve under temperature control
If ΔP too high (approaching flooding), ΔPC cuts steam flow (TC lost)
If sump level too low, low level override cuts steam flow (TC lost)

## Slide 9: Overrides Example 2
Inventory Control System Reconfiguration
LC
FC
LS
TPM
FC
LS
LC
U1SP
OLC
U1SP + Δ
FC
LS
TC
TSP
OTC
TSP - Δ
ΔPC
ΔPSP
Control structure switches between
“In the direction of flow” (nominal)
“In opposite direction of flow” (constrained)

## Slide 10: Split Range Control
Controller output range (0-100%) split to move two or more final control elements
LC
to fuel gas system
to flare
KNOCK-OUT POT
SPLIT RANGE
PC
u
u1
u2

## Slide 11: Selective Control Example
Packed Bed Reactor Hot Spot Temperature Control
PC
HS
Set
Boiler feed water
Steam
LC
TC

## Slide 12: Summary
Valve position control
  Holds a valve position nearly fully open or closed for economic benefit
Override control
  Multiple controllers compete for control valve manipulation
  Necessary for wide process operating space
Split range control
  Splits controller output to adjust two or more control valves
Selective control
  Uses high or low selector blocks
Process understanding and insight is key to proper use of these advanced control strategies